1500 GPM REMOTE CONTROLLED MONITOR

Task Force Tips Typhoon RC, model # Y5-EP1A-Z remote controlled monitor shall be installed. The monitor shall operate on 12 or 24 volt direct current and controlled by a monitor mounted switch panel with functions that control rotation, elevation, nozzle patterns, programmable park and oscillate, auxiliary 1 and auxiliary 2. The monitor shall be compatible with optional wired and wireless control stations and monitor position display.

The electrical components for the monitor shall be waterproof and utilize current limiting and position encoders to protect the drive train at the ends of travel. Monitor shall have ultra flex robotic power cable and include a unique cable guide for 450 degrees of monitor rotation. A six-pin electrical connection for a TFT remote control nozzle shall be provided. The monitor shall be equipped with manual override knobs for use in the event of power failure. The motors and knobs control stainless steel worm gears for rotation and elevation adjustment.

The monitor shall have the following capabilities:

Full horizontal rotation with travel 225 degrees left and right of center;

135 degrees of vertical travel with stops at 90 degrees above horizontal and 45 degrees below horizontal;

Field changeable rotation stops at 45, 90 and 135 degrees left and/or right of center and 45 degrees above and/or 30 degrees below horizontal;

Flow capability of 1500 GPM with 19 PSI of loss;

Maximum operating pressure of 200 PSI

For resistance to corrosion the monitor shall be constructed from hardcoat anodized aluminum with an American red powder coat interior and exterior finish. The discharge elbow shall include an integral stream straightener. A threaded port for an optional pressure gauge shall be provided. The unit shall have a unique serial number and be covered by a five-year warranty.

The monitor shall be configured with a Task Force Tips code RPF threaded inlet to mate with Task Force Tips Extend-A-Gun RC4 telescoping waterway and 3-1/2" male NH outlet.