ELECTRIC VALVE UNDER MONITOR
Task Force Tips VUM, model # AKE122118D electrically controlled monitor valve shall be provided under the monitor. The valve shall be controlled by one or more Task Force Tips monitor controllers using the electronics interface enclosure that is included. The valve can also be controlled with an NFPA compliant slow-close knob which can be configured for left or right hand operation on the valve. A position indicator shall be provided on the valve to allow for quick visualization of the status of the valve in the open, closed or partial positions. The unit shall have a flow capability of up to 2000 GPM with friction loss no more than 6 psi. For maximum corrosion protection the aluminum casting shall be hardcoat anodized, with a silver powder coat internal and external finish. The valve ball shall be stainless steel and have an automatic drain for draining waterway when valve is closed and unpressurized. The unit shall have a unique serial number and be covered by a five-year warranty.
The valve shall be configured with a 4" ANSI 150 flange inlet and TFT Code RPM 22.5° male connection for a Task Force Tips monitor with TFT Code RPF female inlet. Port C1 shall have a left hand elbow quarter turn ball valve with 2-1/2" NH male outlet installed. Ports C2, and C3 shall have blind plugs installed. Port C4 shall have an automatic drain valve for draining the main valve body when unpressurized. All 2-1/2” NH male discharges shall have a 2-1/2” NH female by 1-1/2” NH male thread reducer and a 1-1/2” NH female cap with lanyard.
