
MANUAL VALVE UNDER MONITOR
Task Force Tips VUM, model # AKM132154Z manually controlled monitor valve shall be provided under the monitor. The valve shall be controlled with an NFPA compliant slow-close hand wheel gear operator which can be configured for left or right hand operation. A position indicator shall be provided to allow for quick visualization of the status of the valve in the open, closed or partial positions. The unit shall have a flow capability of up to 2000 GPM with friction loss no more than 6 psi. For maximum corrosion protection the aluminum casting shall be hardcoat anodized, with a silver powder coat internal and external finish. The valve ball shall be stainless. The unit shall have a unique serial number and be covered by a five-year warranty.
The valve shall be configured with a 4" ANSI 150 flange inlet and 4” ANSI 150 flange outlet. Port C1 shall have a left hand elbow quarter turn valve with 2-1/2” NH male outlet installed. Port C2 shall have a blind plug installed. Port C3 shall have a 2-1/2” NH male unvalved outlet installed. Port C4 shall have a straight quarter turn valve with 2-1/2” NH male outlet installed. All 2-1/2” NH male discharges shall have a 2-1/2” NH female by 1-1/2” NH male thread reducer and a 1-1/2” NH female cap with lanyard.

